## Slide 1: ECE 576 – Power System Dynamics and Stability
Prof. Tom Overbye
Dept. of Electrical and Computer Engineering
University of Illinois at Urbana-Champaign
overbye@illinois.edu
Lecture 16: Governors, Multimachine Simulations

## Slide 2: Announcements
Exam average was 85
Homework 5 is assigned today; due on April 3
Read Chapter 7
A useful reference is B. Stott, "Power System Dynamic Response Calculations," Proc. IEEE, vol. 67, pp. 219-241

## Slide 3: IEEEG1
A common stream turbine model, is the IEEEG1, originally introduced in the below 1973 paper
IEEE Committee Report, “Dynamic Models for Steam and Hydro Turbines in Power System Studies,” Transactions in Power Apparatus & Systems, volume 92, No. 6, Nov./Dec. 1973, pp 1904-15
In this model K=1/R
It can be used to represent cross-compound units, with high and low pressure steam
Uo and Uc are rate limits

## Slide 4: IEEEG1
Blocks on the right model the various steam stages
About 12% of WECC governors are currently IEEEG1s
Below figures show two test comparison with this model with one matching well and one not
Image Source: Figs 2-4, 2-6 of IEEE PES, "Dynamic Models for Turbine-Governors in Power System Studies," Jan 2013

## Slide 5: Deadbands
Before going further, it is useful to briefly consider deadbands, with two types shown with IEEEG1 and described in the 2013 IEEE PES Governor Report
The type 1 is an intentional deadband, implemented to prevent excessive response
  Until the deadband activates there is no response, then normal response after that; this can cause a potentially large jump in the response
  Also, once activated there is normal response coming back into range
  Used on input to IEEEG1

## Slide 6: Deadbands
The type 2 is also an intentional deadband, implemented to prevent excessive response
  Difference is response does not jump, but rather only starts once outside of the range
Another type of deadband is the unintentional, such as will occur with loose gears
  Until deadband "engages" there is no response
  Once engaged there is a hysteresis in the response

## Slide 7: Deadband Example: ERCOT
Prior to November 2008, ERCOT required that the governor deadbands be no greater than +/- 0.036 Hz
After 11/3/08 deadbands were changed to +/- 0.0166 Hz
2008 did have two months with the lower values
Image Source: Sydney Niemeyer, NRG, 2/9/10 presentation to Texas Regional Entity (part of ERCOT)

## Slide 8: Gas Turbines
A gas turbine (usually using natural gas) has a compressor, a combustion chamber and then a turbine
The below figure gives an overview of the modeling
Image from IEEE PES, "Dynamic Models for Turbine-Governors in Power System Studies," Jan 2013
HRSG is the heat recovery steam generator (if it is a combined cycle unit)

## Slide 9: GAST Model
Quite detailed gas turbine models exist; we'll just consider the simplest, which is still used some
It is somewhat similar to the TGOV1. T1 is for the fuel valve, T2 is for the turbine, and T3 is for the load limit response based on the ambient temperature (At);
T3 is the delay in measuring the exhaust temperature

## Slide 10: Play-in (Playback) Models
Often time in system simulations there is a desire to test the response of units (or larger parts of the simulation) to particular changes in voltage or frequency
  These values may come from an actual system event
"Play-in" or playback models can be used to vary an infinite bus voltage magnitude and frequency, with data specified in a file
PowerWorld allows both the use of files (for say recorded data) or auto-generated data
  Machine type GENCLS_PLAYBACK can play back a file
  Machine type InfiniteBusSignalGen can auto-generate a signal

## Slide 11: PowerWorld Infinite Bus Signal Generation
Below dialog shows some options for auto-generation of voltage magnitude and frequency variations
Start Time tells when to start; values are then defined for up to five separate time periods
Volt Delta is the magnitude of the pu voltage deviation; Volt Freq is the frequency of the voltage deviation in Hz (zero for dc)
Speed Delta is the magnitude of the frequency deviation in Hz; Speed Freq is the frequency of the frequency deviation
Duration is the time in seconds for the time period

## Slide 12: Example: Step Change Voltage Response
Below graph shows the voltage response for the four bus system for a change in the infinite bus voltage
Case name: B4_SignalGen_IEEEG2

## Slide 13: Simple Diesel Model: DEGOV
Sometimes models implement time delays (DEGOV)
  Often delay values are set to zero
Delays can be implemented either by saving the input value or by using a Pade approximation, with a 2nd order given below; a 4th is common

## Slide 14: DEGOV Delay Approximation
With TD set to 0.5 seconds (which is longer than normal in order to illustrate the delay)

## Slide 15: Hydro Units
Hydro units tend to respond slower than steam and gas units; since early transient stability studies focused on just a few seconds (first or second swing instability), detailed hydro units were not used
  The original IEEEG2 and IEEEG3 models just gave the linear response; now considered obsolete
Below is the IEEEG2; left side is the governor, right side is the turbine and water column
For sudden changes there is actually an inverse change in the output power

## Slide 16: Four Bus with an IEEEG2
Graph below shows the mechanical power output of gen 2 for a unit step decrease in the infinite bus frequency; note the power initially goes down!
Case name: B4_SignalGen_IEEEG2
Physically this is caused by a transient decrease in the water pressure when the valve is opened to increase the water flow

## Slide 17: IEEEG3
This model has a more detailed governor model, but the same linearized turbine/water column model
Because of the initial inverse power change, for fast deviations the droop value is transiently set to a larger value (resulting in less of a power change)
WECC has about 10% of their governors modeled with IEEEG3s

## Slide 18: Washout Filters
A washout filter is a high pass filter that removes the steady-state response (i.e., it "washes it out") while passing the high frequency response
They are commonly used with hydro governors and (as we shall see) with power system stabilizers
With hydro turbines ballpark values for Tw are around one or two seconds

## Slide 19: IEEEG3 Four Bus Frequency Change
The two graphs compare the case response for the frequency change with different Rtemp values
Rtemp = 0.5, Rperm = 0.05
Case name: B4_SignalGen_IEEEG2
Rtemp = 0.05, Rperm = 0.05

## Slide 20: Basic Nonlinear Hydro Turbine Model
Basic hydro system is shown below
  Hydro turbines work be converting the kinetic energy in the water into mechanical energy
  assume the water is incompressible
At the gate assume a velocity of U, a cross-sectional penstock area of A; then the volume flow is A*U=Q;
Source: 9.2, Kundur, Power System Stability and Control, 1994

## Slide 21: Basic Nonlinear Hydro Turbine Model
From Newton's law
As per [a] paper, this equation is normalized to
[a] "Hydraulic Turbine and Turbine Control Models for System Dynamic Studies," IEEE Trans. Power Syst., Feb, 92
T is called the water time constant, or water starting time

## Slide 22: Basic Nonlinear Hydro Turbine Model
With hbase the static head, qbase the flow when the gate is fully open, an interpretation of Tw is the time (in seconds) taken for the flow to go from stand-still to full flow if the total head is hbase
If included the head losses, hloss, vary with the square of the flow
The flow is assumed to vary as linearly with the gate position (denoted by c)

## Slide 23: Basic Nonlinear Hydro Turbine Model
Power developed is proportional to flow rate and head, with a term qnl added to model the fixed turbine (no load) losses
  The term At is used to change the per unit scaling to that of the electric generator

## Slide 24: Model HYGOV
This simple model, combined with a governor, is implemented in HYGOV
About 10% of WECC governors use this model
The gate position (gv) to gate power (pgv) is sometimes represented with a nonlinear curve
Hloss is assumed small and not included

## Slide 25: Linearized Model Derivation
The previously mentioned linearized model can now be derived as

## Slide 26: Four Bus Case with HYGOV
The below graph plots the gate position and the power output for the bus 2 signal generator decreasing the speed then increasing it
Note that just like in the linearized model, opening the gate initially decreases the power output

## Slide 27: PID Controllers
Governors and exciters often use proportional-integral-derivative (PID) controllers
PIDs combine
  Proportional gain, which produces an output value that is proportional to the current error
  Integral gain, which produces an output value that varies with the integral of the error; this will eventually drive the error to zero
  Derivative gain, which acts to predict the system behavior. This can enhance system stability, but it can be quite susceptible to noise

## Slide 28: PID Example: Position Control
Say we wish to get an object to a position in 1-dimensional space by controlling its acceleration (force)
  Error is distance from desired position
  Control is speed
With just proportional control, acceleration will be decreasing, but we'd reach maximum speed at the desired point, overshooting
With derivative control, we'll be slowing down, avoiding the overshoot
The integral term will make sure we stay at the desired point

## Slide 29: HYG3
The HYG3 models either a PID or a double derivative
Looks more complicated than it is since depending on cflag only one of the upper paths is used