## Slide 1: ECE 576 – Power System Dynamics and Stability
Prof. Tom Overbye
University of Illinois at Urbana-Champaign
overbye@illinois.edu
Lecture 28: Power System Stabilizer

## Slide 2: Announcements
Read Chapters 8 and 9
Homework 8 should be completed before final but need not be turned in
Final is Wednesday May 14 at 7 to 10pm
Key papers for book's approach on stabilizers are
  F.P. DeMello and C. Concordia, "Concepts of Synchronous Machine Stability as Affected by Excitation Control, IEEE Trans. Power Apparatus and Systems, vol. PAS-88, April 1969, pp. 316-329
  W.G. Heffron and R.A. Philips, "Effects of Modern Amplidyne Voltage Regulator in Underexcited Operation of Large Turbine Generators," AIEE, PAS-71, August 1952, pp. 692-697

## Slide 3: Functions of a PSS
PSS adds a signal to the excitation system proportional to speed deviation. This adds positive damping
  Other inputs, like power, voltage or acceleration, can be used
  Signal is generated locally from the shaft.
Both local mode and inter-area mode can be damped. When oscillation is observed on a system or a planning study reveals poorly damped oscillations, use of participation factors helps in identifying the machine(s) where PSS has to be located.
Tuning of PSS regularly is important.
Modal Analysis technique forms the basis for multi-machine systems.

## Slide 4: Example PSS
An example single input stabilizer is shown below (IEEEST)
  The input is usually the generator shaft speed deviation, but it could also be the bus frequency deviation, generator electric power or voltage magnitude
VST is an input into the exciter

## Slide 5: Example PSS
Below is an example of a dual input PSS (PSS2A)
  Combining shaft speed deviation with generator electric power is common
  Both inputs have washout filters to remove low frequency components of the input signals
IEEE Std 421.5 describes the common stabilizers

## Slide 6: PSS Tuning: Basic Approach
The PSS parameters need to be selected to achieve the desired damping through a process known as tuning
The next several slides present a basic method using a single machine, infinite bus (SMIB) representation
Start with the linearized differential, algebraic model with controls u added to the states
If D is invertible then

## Slide 7: SMIB System (Flux Decay Model)
Process is introduced using an SMIB with a flux decay machine model and a fast exciter
~

## Slide 8: Stator Equations
Assume Rs=0, then the stator algebraic equations are:

## Slide 9: Network Equations
The network equation is (assuming zero angle at the infinite bus and no local load)
Simplifying,
~

## Slide 10: Complete SMIB Model
Stator equations
Network equations
~
Machine equations

## Slide 11: Linearization of SMIB Model
Notice this is equivalent to a generator at the infinite bus with modified resistance and reactance values

## Slide 12: Linearization (contd)
Final Steps involve
Linearizing Machine Equations
Substitute (1) in the linearized equations of (2).

## Slide 13: Linearization of Machine Equations
Substitute (3) in (2) to get linearized model.
Symbolically we have

## Slide 14: Linearized SMIB Model
Excitation system is yet to be included.
K1 – K4 constants are defined on next slide

## Slide 15: K1 – K4 Constants
K1 – K4 only involve machine and not the exciter.

## Slide 16: Including Terminal Voltage
The change in the terminal voltage magnitude also needs to be include since it is an input into the exciter

## Slide 17: Computing
While linearizing the stator algebraic equations, we had
Substitute this in expression for DVt to get

## Slide 18: Heffron–Phillips Model
Add a fast exciter with a single differential equation
Linearize
This is then combined with the previous three differential equations to give
SMIB Model

## Slide 19: Block Diagram
K1 – K6 are affected by system loading and Xe

## Slide 20: Numerical Example
Consider an SMIB system with Zeq = j0.5, Vinf = 1.05, in which in the power flow the generator has S = 54.34 – j2.85 MVA with a Vt of 115
  Machine is modeled with a flux decay model with (pu, 100 MVA) H=3.2, T'do=9.6, Xd=2.5, Xq=2.1, X'd=0.39, Rs=0, D=0
Saved as case B2_PSS_Flux (but only available in v18)

## Slide 21: Initial Conditions
The initial conditions are

## Slide 22: Add an EXST1 Exciter Model
Set the parameters to KA = 400, TA=0.2, all others zero with no limits and no compensation
Hence this simplified exciter is represented by a single differential equation
Vs is the input from the stabilizer, with an initial value of zero

## Slide 23: Initial Conditions (contd)
From the stator algebraic equation,

## Slide 24: Computation of K1 – K6 Constants
The formulas are used.

## Slide 25: Effect of Field Flux on System Stability
With constant field voltage, i.e. DEfd=0, from the block diagram
  K2, K3, and K4 are usually positive.
On diagram Dv is used to indicate what we've been calling Dwpu

## Slide 26: Effect of Field Flux on System Stability
For low frequencies and in steady-state, as s=jw goes to zero, then
Hence field flux variation due to Dd feedback (armature reaction) introduces negative synchronizing torque

## Slide 27: Effect of Field Flux on System Stability
At higher frequencies the denominator is dominated by the K3T'dos term so
This is a phase with Dw(jDd)
Hence Efd results in a positive damping component.

## Slide 28: Effect of Field Flux on System Stability
In general, positive damping torque and negative synchronizing torque due to Efd at typical oscillation frequencies (1-3 Hz).

## Slide 29: Effect of Field Flux
There are situations when K4 can become negative.
Case1. A hydraulic generator without a damper winding, light load (d is small) and connected to a line with high Re/Xe ratio and a large system.
Case 2. Machine is connected to a large local load, supplied partly by generator and partly by remote large system.
If K4 < 0 then the damping due to Efd is negative

## Slide 30: Effect of Excitation System
Ignore dynamics of AVR & KA >> 0
Gain through T'do is -(K4+KAK5)K3
If K5 < 0 then gain becomes positive.
DVREF = 0
Large enough K5 may make system unstable

## Slide 31: Numerical Example (Effect of K5)
Test system 1 Test System 2
Eigen Values
Test System 1 Test System 2
unstable

## Slide 32: Addition of PSS Loop
The impact of a PSS can now be considered in which the shaft speed signal is fed through the PSS transfer function G(s) to the excitation system.
To analyze effect of PSS signal assume Dd, DVREF=0

## Slide 33: PSS Contribution to Torque
(for usual range
of constants)

## Slide 34: PSS Contribution to Torque
For high gain KA
If PSS were to provide pure damping (in phase with wpu), then ideally,
Practically G(s) is a combination of lead and lag blocks.
i.e. pure lead function

## Slide 35: PSS Block Diagram
Provide damping over the range of frequencies (0.1-2 Hz)
“Signal wash out” (Tw) is a high pass filter
  TW is in the range of 5 to 20 seconds
Allows oscillation frequencies to pass unchanged.
Without it, steady state changes in speed would modify terminal voltage.

## Slide 36: Criteria for Setting PSS Parameters
KPSS determines damping introduced by PSS.
T1, T2, T3, T4 determine phase compensation for the phase lag present with no PSS.
A typical technique is to compensate for the phase lag in the absence of PSS such that the net phase lag is:
  Between 0 to 45 from 0.3 to 1 Hz.
  Less than 90 up to 3 Hz.
Typical values of the parameters are:
  KPSS is in the range of 0.1 to 50
  T1 is the lead time constant, 0.2 to 1.5 sec
  T2 is the lag time constant, 0.02 to 0.15 sec
  T3 is the lead time constant, 0.2 to 1.5 sec
  T4 is the lag time constant, 0.02 to 0.15 sec

## Slide 37: Design Procedure
The desired stabilizer gain is obtained by finding the gain at which the system becomes unstable by root locus study.
The washout time constant TW is set at 10 sec.
KPSS is set at (1/3)K*PSS, where (1/3)K*PSS is the gain at which the system becomes unstable.
There are many ways of adjusting the values of T1, T2, T3, T4
Frequency response methods are recommended.

## Slide 38: Design Procedure Using the Frequency-Domain Method
Step 1: Neglecting the damping due to all other sources, find the undamped natural frequency in rad/sec of the torque - angle loop from:
Step 2: Find the phase lag of

## Slide 39: PSS Design (contd)
Step 3:
Adjust the phase lead of G(s) such that
Ignoring the washout filter whose net phase
contribution is approximately zero.

## Slide 40: PSS Design (contd)
Knowing wn and GEP(j wn) we can select T1. T2 can be chosen as some value between 0.02 to 0.15 sec.
Step 4: Compute K*PSS, the gain at which the system becomes unstable, using the root locus. Then have
The char. equation is
The damping ratio is
Alternative Procedure
X
X
Damping ratio

## Slide 41: PSS Design (contd)
The characteristic roots are:

## Slide 42: PSS Design (contd)
Since the phase lead of G(s) cancels phase lag due to GEP(s) at the oscillatory frequency, the contribution of PSS through GEP(s) is a pure damping torque with a damping coefficient DPSS

## Slide 43: PSS Design (contd)
The washout filter should not have any effect on phase shift or gain at the oscillating frequency.
A large value of TW is chosen so that sTW is much larger than unity.
Choose
Hence, its phase contribution is close to zero. The PSS will not have any effect on the steady state behavior of of the system since in steady state Dwpu=0

## Slide 44: Example
Without the PSS, the A matrix is
The electromechanical mode l1,2 is poorly damped.
Instead of a two-stage lag lead compensator, assume a single-stage lag-lead PSS. Assume that the damping D in the torque-angle loop is zero.
The input to the stabilizer is Dwpu. An extra state equation will be added. The washout stage is omitted.

## Slide 45: Example (contd)
The added differential equation is then

## Slide 46: Example (contd)
Note the improvement of the electromechanical mode l1,2

## Slide 47: Example (industry)
CONVERT TO SMIB (RETAIN G16)

## Slide 48: Example (contd)
Largest Participation by angle and speed states.
E.M. Mode has f = 0.5688 Hz
The participator for this mode is
*
*
Poorly damped
Exciter mode
well damped
Convert these into
magnitudes
Turbine Governor States

## Slide 49: Root Locus
If G(s) (Transfer function of PSS) is a real gain, it will add pure damping Root Locus Study (with KPSS = 10).

## Slide 50: Phase Compensation
Ideal phase lead.
PSS phase lead.
Washout does not add
much phase lead.

## Slide 51: Root Locus with PSS

## Slide 52: Eigenvalues with PSS
Note Improvement in Damping Ratio of E.M Mode
from 0.05 to 0.123